## Heat Loss Estimate
HANNAH PLUMBING & HEATING LTD - WHOLE BUILDING HEAT LOSS ESTIMATE
The Beresford Building, 460 Sauchiehall Street, Glasgow G2 3JW (Cat. B listed, 1938, converted to flats c.2002-08)
BUDGET ESTIMATE ONLY - whole-building peak space-heating load by simple U x A x dT + ventilation method (BS EN 12831 style). No drawings or survey: geometry and U-values are ASSUMED. Yellow cells are editable; replace with measured figures before sizing plant. Excludes domestic hot water.
1. DESIGN CONDITIONS | Value |  | Source / note
External design temperature (°C) | -5.6 |  | Glasgow (Bishopton) 99.6% - CIBSE Guide A 2015 Tbl 2.5, as used by MCS heat load calculator
Mean internal temperature, flats (°C) | 20 |  | Whole-flat average (living 21, bedrooms 18, baths 22)
Design temperature difference dT (K) |  |  | Calculated
Floor below lowest flat - temp factor (0-1) | 0.5 |  | Ground floor assumed commercial/entrance, partly heated: 0.5 x dT. Set 1.0 if open/unheated, 0 if fully heated.
2. BUILDING GEOMETRY (ASSUMED - CHECK) | Value |  | Basis
Number of flats | 121 |  | Published conversion figure is 112-121 flats; not used in the calc, only for the per-flat figure
Heated residential floors | 9 |  | Sources say 8-10 storeys; assumed ground = commercial/entrance + 9 floors of flats
Gross internal area per floor (m²) | 850 |  | ESTIMATE: ~13 flats/floor x ~53 m² avg (EPCs 40-63 m²) + circulation
External wall perimeter per floor (m) | 150 |  | ESTIMATE - measure from OS map / drawings
Floor-to-floor height (m) | 3 |  | Typical 1930s hotel
Internal ceiling height (m) | 2.7 |  | For ventilation volume
Glazing % of gross external wall | 30 |  | Horizontal bands of Art Deco windows - check on elevations
Roof area (m²) |  |  | Assumed equal to the floor plate (flat roof)
Total heated floor area (m²) |  |  | Calculated
Gross external wall area (m²)
Glazing area (m²)
Opaque wall area (m²)
Heated volume (m³)
3. FABRIC & VENTILATION | Scenario A Conversion upgraded | Scenario B Little upgrade | Note
Wall U-value (W/m²K) | 0.6 | 1.5 | A: solid brick with insulated dry-lining (2000s conversion). B: original solid brick/tile cladding
Window U-value (W/m²K) | 2 | 2.8 | A: double glazed (listed-sympathetic). B: early double glazing / secondary
Roof U-value (W/m²K) | 0.25 | 0.6 | A: insulated at conversion. B: concrete flat roof, little insulation
Floor over commercial U-value (W/m²K) | 0.5 | 1 | Concrete slab to ground floor / entrance
Thermal bridging y-value (W/m²K) | 0.1 | 0.15 | Concrete slab edges / lintels, applied to external area
Air change rate (ach) | 0.5 | 1 | A: sealed windows + extract fans. B: draughty older windows
4. HEAT LOSS COEFFICIENTS (W/K) | Scenario A | Scenario B
Walls
Windows
Roof
Floor over ground floor (x temp factor)
Thermal bridging
Fabric total
Ventilation (0.33 x ach x V)
TOTAL HEAT LOSS COEFFICIENT
5. PEAK DESIGN HEAT LOSS | Scenario A | Scenario B | Note
Fabric loss (kW)
Ventilation loss (kW)
TOTAL PEAK SPACE-HEATING LOAD (kW) |  |  | Whole building at design conditions
Load per m² of heated floor (W/m²) |  |  | Sanity check: refurbished flats ~25-40, older stock 50+
Average per flat (kW) |  |  | Top-floor / corner flats will be higher, inner flats lower
Suggested plant output incl. 10% margin (kW) |  |  | Space heating only - add DHW (stored or HIU instantaneous) separately
NOTES & QUALIFICATIONS
1. Not a room-by-room MCS / BS EN 12831 calculation - for budget or feasibility only. Plant must be sized from a full room-by-room calc once surveyed.
2. Existing heating varies by flat: EPCs and listings show electric underfloor heating in some flats and underfloor heating off a communal (gas) system in others. Confirm what the building actually has before pricing.
3. Category B listed - external wall insulation and window replacement are restricted, so the fabric is unlikely to be much better than Scenario A.
4. No allowance for internal or solar gains, intermittent heating or pipework losses on a communal system (typically add 10-20% distribution loss for communal heat networks).
5. Geometry figures are desk estimates. Biggest swings: floor area, number of storeys, glazing % and air change rate. Update the yellow cells and everything else recalculates.