## Summary
HANNAH PLUMBING & HEATING LTD - LABOUR ONLY PRICING
NLC - Pivot Community Centre (RAAC works) ¦ Client: Procast (David Inch) ¦ Design: Harley Haddow job 313160
Labour only - all materials free-issue by others. Quantities measured from drawings 313160-HAH-XX-00-D-M-05330 P01, 05630 P02, 05230 P02 (tender issue Nov 2025). Prices exclude VAT.
Pricing inputs (yellow cells are editable):
Labour rate per hour (£) | 50 |  |  | Same rate as Life Church tender
Wastage / offsets allowance on measured pipe (%) | 10% |  |  | Covers offsets, crossovers, fittings not shown on 1:100 plans
Contingency on total (%) | 5% |  |  | Drawings marked 'do not scale' - measured take-off ±10%
Hours per working day | 8 |  |  | Used for programme days only
Operatives on site | 2 |  |  | Used for programme days only
Section | Labour hrs | Total (£) | % of total | Source
A - Hot & cold water pipework (copper) | 275.2882 | 13764.41 | 22.72% | Pipework sheet
B - LTHW heating pipework (stainless) | 355.0239 | 17751.195 | 29.3% | Pipework sheet
C - Above-ground drainage pipework (PVCu) | 46.233 | 2311.65 | 3.816% | Pipework sheet
D - Preliminaries | 24 | 1200 | 1.981% | Fittings & Items sheet
E - Hot & cold water - connections, plant & commissioning | 165 | 8250 | 13.62% | Fittings & Items sheet
F - Heating - emitters, valves & commissioning | 224 | 11200 | 18.49% | Fittings & Items sheet
G - Drainage - connections & items | 90 | 4500 | 7.429% | Fittings & Items sheet
H - Gas (provisional) | 32 | 1600 | 2.641% | Fittings & Items sheet
Sub-total | 1211.5451 | 60577.255
Contingency |  | 3028.8627
LABOUR-ONLY TENDER TOTAL (ex VAT) |  | 63606.1177
Total labour hours | 1211.5451
Programme (working days for gang) | 75.7216
Effective £ per man-day | 400
Measured pipework totals (excl. wastage)
Copper - hot, cold & secondary return (m) | 816.3
Stainless - LTHW heating (m) | 1151.7
PVCu drainage (m) - rough | 126
Key qualifications / queries to raise with Procast
• Labour only - all pipe, fittings, valves, brackets, insulation, sanitaryware and plant free-issue by others.
• Heating priced in stainless steel press (per Procast) - drawing notes still say mild steel; stainless OD sizes assumed 42/35/28/22/15.
• Drops to low level assumed 2.5m - ceiling heights not on drawings. Each 0.5m change = approx. ±54m heating / ±27m water.
• Library water feed (22mm H/C/R 'continues to serve library') - route not drawn; excluded, approx. 20m per service if required.
• CWST size discrepancy: drawing 3248x3248x2916 vs schedule 2248x2248x2566 (both 8,000L). Tank erection by supplier assumed.
• Thermal insulation, fire-stopping, builder's work, boxing-in and access hatches by others unless instructed.
• Electrical supplies & interlocks (booster set, fan convectors, gas safety system, panel heaters PH01) by electrician.
• Ventilation (MVHR units, fans, ductwork, cowls) excluded.
• Gas pipe length is PROVISIONAL (30m) - drawing 05430 not measured.
• Take-off measured from tender drawings marked 'do not scale' - accuracy approx. ±10%; re-measure from construction issue.

## Pipework
PIPEWORK - measured take-off and labour build-up
Blue = measured from drawings (edit only if you re-measure). Yellow = labour hours per metre - ESTIMATED norms for install in ceiling void incl. brackets, fittings & valves on the run; adjust to suit your gang.
Ref | Service / description | Size | Measured (m) | Inc. wastage (m) | Hrs / m | Labour hrs | Rate £ / m | Total (£) | Notes
A | HOT & COLD WATER - COPPER (dwg 05330)
A1 | Boosted / tank cold water (BCWS) | 35mm | 27.4 | 30.14 | 0.48 | 14.4672 | 24 | 723.36 | Plant room main + first section of south main
A2 | Boosted / tank cold water (BCWS) | 28mm | 54.9 | 60.39 | 0.38 | 22.9482 | 19 | 1147.41 | East main, east corridor riser, south main lower; incl. 7.5m allowance where drawing is broken at accessible WC
A3 | Boosted / tank cold water (BCWS) | 22mm | 99 | 108.9 | 0.3 | 32.67 | 15 | 1633.5 | Branches + 9 No. 22mm drops @ 2.5m
A4 | Boosted / tank cold water (BCWS) | 15mm | 106.6 | 117.26 | 0.25 | 29.315 | 12.5 | 1465.75 | Tails to fittings + 9 No. 15mm drops @ 2.5m
A5 | Mains cold water (MCWS) - incoming to tank | 35mm | 53.1 | 58.41 | 0.48 | 28.0368 | 24 | 1401.84 | Incoming main rises at SW corner, runs at high level to CWST
A6 | Hot water flow (HWSF) | 35mm | 7 | 7.7 | 0.48 | 3.696 | 24 | 184.8 | Plant room exit (88 l/s section)
A7 | Hot water flow (HWSF) | 28mm | 62 | 68.2 | 0.38 | 25.916 | 19 | 1295.8 | Mains; incl. 7.5m allowance at accessible WC break
A8 | Hot water flow (HWSF) | 22mm | 104.6 | 115.06 | 0.3 | 34.518 | 15 | 1725.9 | Branches + 7 No. 22mm drops @ 2.5m
A9 | Hot water flow (HWSF) | 15mm | 81.5 | 89.65 | 0.25 | 22.4125 | 12.5 | 1120.625 | Tails + 11 No. 15mm drops @ 2.5m
A10 | Secondary return (HWSR) | 22mm | 13.7 | 15.07 | 0.3 | 4.521 | 15 | 226.05 | Plant room section
A11 | Secondary return (HWSR) | 15mm | 206.5 | 227.15 | 0.25 | 56.7875 | 12.5 | 2839.375 | Return throughout + 18 No. drops @ 2.5m + 7.5m break allowance
| Sub-total A |  | 816.3 | 897.93 |  | 275.2882 |  | 13764.41
B | LTHW HEATING - STAINLESS STEEL PRESS (dwg 05630)
B1 | LTHW flow & return (VT circuit from plant) | 42mm (40NB) | 95.1 | 104.61 | 0.5 | 52.305 | 25 | 2615.25 | Drawing sizes are steel NB - stainless OD equivalent shown; confirm with Procast
B2 | LTHW flow & return | 35mm (32NB) | 128.6 | 141.46 | 0.42 | 59.4132 | 21 | 2970.66 | VT to library, kitchen branch, south main
B3 | LTHW flow & return (CT circuit) | 28mm (25NB) | 83.7 | 92.07 | 0.33 | 30.3831 | 16.5 | 1519.155 | CT to library + south main section
B4 | LTHW flow & return | 22mm (20NB) | 156.4 | 172.04 | 0.27 | 46.4508 | 13.5 | 2322.54 | Sub-mains / branches
B5 | LTHW flow & return - branches & low-level runs | 15mm | 417.9 | 459.69 | 0.22 | 101.1318 | 11 | 5056.59 | Branches to radiators / fan convectors
B6 | LTHW drops to emitters (F&R) | 15mm | 270 | 297 | 0.22 | 65.34 | 11 | 3267 | 54 emitters x 2 pipes x 2.5m assumed drop - ceiling height not on drawings
| Sub-total B |  | 1151.7 | 1266.87 |  | 355.0239 |  | 17751.195
C | ABOVE GROUND DRAINAGE - PVCu (dwg 05230) - ROUGH
C1 | Soil branches (horizontal) | 110mm | 25 | 27.5 | 0.35 | 9.625 | 17.5 | 481.25 | Approx. split of ~61m measured horizontal drainage
C2 | Waste branches | 40mm | 12 | 13.2 | 0.25 | 3.3 | 12.5 | 165 | Approx. split
C3 | Waste branches | 32mm | 24 | 26.4 | 0.22 | 5.808 | 11 | 290.4 | Approx. split
C4 | Pre-insulated SVPs (11 No. through roof) | 110mm | 55 | 60.5 | 0.4 | 24.2 | 20 | 1210 | 11 stacks x ~5m assumed (ground to above roof)
C5 | Stub stacks (8 No.) | 50/75mm | 10 | 11 | 0.3 | 3.3 | 15 | 165 | 8 stub stacks x ~1.2m
| Sub-total C |  | 126 | 138.6 |  | 46.233 |  | 2311.65

## Fittings & Items
FITTINGS, PLANT, CONNECTIONS & COMMISSIONING - labour build-up
Blue quantities are counted from the drawings / schedules. Yellow hours per item are ESTIMATES - adjust to suit. Set qty to 0 to omit an item.
Ref | Description | Unit | Qty | Hrs each | Labour hrs | Total (£) | Notes / qualifications
D | PRELIMINARIES
D1 | RAMS, inductions, site set-up, setting out & co-ordination drawings | item | 1 | 16 | 16 | 800 | Contractor to produce co-ordinated installation drawings (dwg note)
D2 | Pre-start survey of existing M&E services (required by dwg notes) | item | 1 | 8 | 8 | 400
| Sub-total D |  |  |  | 24 | 1200
E | HOT & COLD WATER - CONNECTIONS & PLANT
E1 | Connect WC (cold feed, isolation valve) | no | 27 | 0.75 | 20.25 | 1012.5 | Count from drainage notes; sanitaryware fixing NOT included - confirm whose scope
E2 | Connect WHB incl. TMV3 (Oventrop Brawa-mix), isolation, strainers | no | 24 | 1.75 | 42 | 2100 | TMV to every WHB & sink per dwg note 16
E3 | Connect sink incl. TMV3, isolation | no | 7 | 1.75 | 12.25 | 612.5
E4 | Connect shower (H&C, isolation) | no | 11 | 1.5 | 16.5 | 825 | Shower valves assumed thermostatic; check spec
E5 | Hot water return commissioning valves (Oventrop Aquastrom T Plus) | no | 18 | 0.5 | 9 | 450 | One per drop assumed
E6 | Install & connect booster set BP01 (Grundfos Hydro Multi-E) on AV mounts, flexible connections | item | 1 | 12 | 12 | 600 | Electrical supply by others
E7 | Connect 8,000L CWST - float valve, outlets, screened overflow / warning / drain-down | item | 1 | 16 | 16 | 800 | Tank erection by tank supplier assumed - CHECK. Tank size discrepancy dwg 3248 vs schedule 2248
E8 | Plant room pipework not shown on plan (35 suction, 54 overflow/drain, 28 warning) | m | 20 | 0.45 | 9 | 450 | Allowance only - schematic on drawing
E9 | Tie-in to existing water services / incoming main | no | 2 | 4 | 8 | 400
E10 | Pipework labelling to BS 1710 | item | 1 | 8 | 8 | 400
E11 | Pressure test, flush, chlorinate & certify (BS EN 806 / L8) | item | 1 | 12 | 12 | 600 | Lab sample fee by others (labour only)
| Sub-total E |  |  |  | 165 | 8250
F | HEATING - EMITTERS, VALVES, COMMISSIONING
F1 | Hang & connect LST radiator incl. TRV, LSV, cover (R01-R20) | no | 48 | 2.5 | 120 | 6000 | Merriot Protecta - qty from equipment schedule
F2 | Hang & connect fan convector (FC01 x5, FC02 x1) incl. remote-sensor TRV | no | 6 | 3 | 18 | 900 | Electrical connection by others
F3 | Commissioning sets CS01-CS10 | no | 10 | 1.5 | 15 | 750
F4 | Branch isolation valves (pairs) - on drops/branches | pair | 30 | 0.5 | 15 | 750 | Approx. count from dwg 05630 - verify
F5 | AAVs at high points / drain cocks at low points | no | 20 | 0.4 | 8 | 400 | Allowance
F6 | Tie-in to existing LTHW in plant room (CT & VT circuits) | no | 2 | 6 | 12 | 600 | Drain-down / refill of existing system included
F7 | Tie-in to existing pipework in library (CT & VT) | no | 2 | 4 | 8 | 400
F8 | Tie-in fan convector circuit to existing in plant room | no | 1 | 4 | 4 | 200
F9 | Pressure test, flush, fill, vent, balance & commission | item | 1 | 24 | 24 | 1200 | Water treatment chemicals by others
| Sub-total F |  |  |  | 224 | 11200
G | DRAINAGE - ITEMS
G1 | SVP roof termination - weather collar & bird cage, access door | no | 11 | 1.5 | 16.5 | 825 | Weathering by roofer (dwg note 10)
G2 | Stub stack AAV & access, connect to below-ground | no | 8 | 1 | 8 | 400
G3 | 110mm pop-up connection to below-ground | no | 2 | 1 | 2 | 100
G4 | WC pan connection | no | 27 | 0.5 | 13.5 | 675
G5 | Basin / sink trap & waste connection | no | 31 | 0.5 | 15.5 | 775 | 24 WHB + 7 sinks
G6 | Shower gully - install & connect to existing BG pop-up | no | 11 | 1.5 | 16.5 | 825
G7 | Grease separator on kitchen drainage line (install & connect) | no | 1 | 4 | 4 | 200 | Unit supply & sizing by others
G8 | Condensate tundishes / waterless traps to SVP | no | 4 | 0.75 | 3 | 150 | Allowance
G9 | Intumescent collars / fire sleeves | no | 20 | 0.25 | 5 | 250 | Allowance - fire-stopping by others?
G10 | Test above-ground drainage | item | 1 | 6 | 6 | 300
| Sub-total G |  |  |  | 90 | 4500
H | GAS (dwg 05430 - not measured)
H1 | Gas pipework meter to kitchen - black steel, screwed (PROVISIONAL) | m | 30 | 0.6 | 18 | 900 | Length NOT measured - drawing 05430 not uploaded. Re-measure.
H2 | Kitchen gas safety system - solenoid, panel, detector, e-stop (mechanical install) | item | 1 | 6 | 6 | 300 | Wiring & interlock to fans / fire alarm by electrician
H3 | Strength / tightness test, purge, commission & certify (IGEM UP-1/UP-4), iso drawings | item | 1 | 8 | 8 | 400
| Sub-total H |  |  |  | 32 | 1600