## Quote
HANNAH PLUMBING & HEATING LTD - QUOTATION BUILD-UP
Aberdeen - Boiler replacement: remove Ideal Concord 100kW, install 2 No. Worcester Bosch Greenstar 8000 35kW system boilers with plate heat exchanger
Prices exclude VAT. Material rates are ESTIMATED trade prices - confirm with merchant before issuing. Site survey not yet carried out (see Qualifications).
Pricing inputs (yellow cells are editable):
Labour rate per hour (£) |  |  | 50 | Same rate as Life Church / Pivot Centre
Materials mark-up (%) |  |  | 15% | Same as Life Church tender
Mark-up on electrician (%) |  |  | 0 | Set to e.g. 0.10 to add 10% handling
Contingency on total (%) |  |  | 5% | Unsurveyed - flue route, gas supply, condition of existing system
Operatives on site |  |  | 2 | Used for programme days only
Hours per working day |  |  | 8 | Used for programme days only
Ref | Description | Labour hrs | Labour (£) | Materials inc. mark-up (£) | Total (£) | Notes
1 | Preliminaries - RAMS, gas & site survey, set-up, protection, consumables | 6 |  |  |  | Allow for commercial gas paperwork
2 | Isolate, drain down, cap gas, disconnect & remove Ideal Concord 100kW + existing flue; break down & dispose | 16 |  |  |  | Concord is sectional cast iron - heavy, 2-man strip-out
3 | Supply & fix 18mm plywood backing board to plant room wall | 4
4 | Hang 2 No. Worcester Greenstar 8000 35kW system boilers incl. flue kits & terminals | 14 |  |  |  | Assumes straight-through / short horizontal flues
5 | Primary pipework: boilers to plate heat exchanger incl. 2 No. magnetic filters, valves, pressurisation | 20 |  |  |  | Sealed primary circuit on boiler side
6 | Supply & install Worcester plate heat exchanger; connect secondary (existing system) incl. new secondary pump | 12 |  |  |  | Separates new boilers from old system
7 | Gas pipework to both boilers incl. isolation valves; tightness test & purge | 6 |  |  |  | Assumes existing gas supply adequate for 70kW
8 | Condensate pipework to suitable drain (2 No.) | 3
9 | Insulate all new pipework in plant room | 6
10 | Chemical clean / flush existing system, fill, inhibit (secondary & primary) | 6 |  |  |  | Powerflush of old system NOT included
11 | Commission boilers, Benchmark, commercial gas certification, handover & demo | 7
12 | Electrical works - subcontract electrician (supplies, controls, wiring of boilers/pump) |  |  | 1000 |  | Fixed price from electrician
13 | Travel & accommodation allowance - Aberdeen (fuel + digs for 2 men) |  |  | 1000 |  | Set to 0 if local / not staying over
Sub-total
Contingency
QUOTE TOTAL (ex VAT)
VAT @ 20%
QUOTE TOTAL (inc VAT)
Programme (days on site)
Qualifications / exclusions
- Price subject to site survey - flue route, plant room access & gas meter/supply capacity not yet checked.
- Assumes existing gas supply & meter adequate for 2 x 35kW (70kW). Gas upgrade / new meter excluded.
- Assumes horizontal flues through wall within standard lengths. Vertical/plume or extended flues extra.
- If this is non-domestic premises (likely, given an existing 100kW Concord), the engineer needs the relevant commercial gas tickets - confirm before pricing labour.
- Powerflush of existing system, radiator/valve replacement and asbestos removal excluded.
- Builder work (making good, decoration, core drilling through stone) excluded unless stated.
- Electrical works by subcontract electrician as priced (£1,000) - confirm their scope covers controls/wiring centre.
- Boiler & PHE prices to be confirmed with merchant - Worcester PHE model/size to be confirmed against heat load.

## Materials
Materials - ESTIMATED trade prices (net), check with merchant
Ref | Item | Qty | Unit | Rate (£) | Total (£)
1 | Consumables - solder, flux, PTFE, fixings, protection | 1 | lot | 150
2 | Disposal of old boiler / scrap & skip share | 1 | item | 150
2 | Gas cap / stop ends, drain hoses | 1 | lot | 25
3 | 18mm WBP plywood 2440x1220 | 2 | sht | 45
3 | Fixings / plugs | 1 | lot | 20
4 | Worcester Bosch Greenstar 8000 Life 35kW system boiler | 2 | no | 2400
4 | Flue kit (horizontal) | 2 | no | 150
4 | Flue extension allowance | 1 | item | 150
5 | Magnetic filter 28mm (Worcester Greenstar System Filter / MagnaClean) | 2 | no | 120
5 | Copper tube & fittings 28/35mm (primary) | 1 | lot | 600
5 | Isolation valves, drain-offs, AAVs, gauges, NRVs | 1 | lot | 300
5 | Expansion vessel + filling loop for sealed primary | 1 | item | 120
6 | Worcester Bosch plate heat exchanger kit (sized ~70kW) | 1 | no | 1200
6 | Secondary circulating pump (Grundfos Magna1 or equal) + valves | 1 | no | 550
6 | Copper tube & fittings 28/35mm (secondary) | 1 | lot | 300
7 | Gas pipe & fittings, gas isolation valves | 1 | lot | 250
8 | Condensate pipe, fittings & clips | 1 | lot | 60
9 | Pipe insulation (Armaflex / Class O) & tape | 1 | lot | 250
10 | Fernox F3 cleaner + F1 inhibitor | 1 | lot | 120
TOTAL MATERIALS (net)