## Tender
HANNAH PLUMBING & HEATING LTD - TENDER RETURN
Life Church - Ground Floor Fit Out, 6-8 High Street, Paisley PA1 2YA ¦ Main contractor: Woodvale Projects Ltd
Priced to BOQ Rev3 (Clarification No.2, 30/09/26). Plumbing & drainage package. All prices exclude VAT (domestic reverse charge applies).
Pricing inputs (yellow cells are editable):
Labour rate per hour (£) |  |  | 50
Materials mark-up (%) |  |  | 15%
Extra O&P on labour (%) - 0% as hourly rate is the billed rate |  |  | 0%
BOQ Ref | Description | Unit | Qty | Rate (£) | Total (£) | Notes / Qualifications
P1 | Plumbing preliminaries - RAMS, site set-up, travel/parking (Paisley town centre), consumables | item | 1
2.12 | Disconnect, remove & dispose of existing toilet, sink and plumbing pipework/fittings in WC's | item | 1
2.13 | Terminate and cap building services as required (plumbing services only) | item | 1 |  |  | Electrical by others
14.01 | WC adjacent to kitchen - supply & install sanitaryware (soft-close WC, standalone basin) | Budget | 1 |  |  | Standard commercial range (Twyford/Armitage Shanks or equal)
14.03 | Soap dispenser attached to wall | item | 1
14.05 | WC adjacent to rear staircase - supply & install sanitaryware (soft-close WC, standalone basin) | Budget | 1 |  |  | Standard commercial range
14.07 | Soap dispenser attached to wall | item | 1
14.10 | Accessible WC (cafe) - Doc M service pack, supply & install | item | 1 |  |  | Doc M pack incl. rails, basin, lever tap
14.11 | Accessible WC - wall-hung pan: concealed frame & cistern (extra over Doc M pack) | Budget | 1 |  |  | Omit if close-coupled Doc M pan acceptable
14.14 | Soap dispenser attached to wall | item | 1
15.01 | Drainage above ground - accessible WC (WC & basin) incl. NEW 110mm SVP, AAV & access | item | 1
15.02 | Drainage above ground - WC facilities (WC & basin) into existing SVP | item | 1 |  |  | Assumes existing SVP sound; connection to cast iron via transition coupling
15.03 | Drainage above ground - kitchen (sink, WHB, dishwasher) into existing SVP | P.Sum | 1 |  |  | Grease trap supply EXCLUDED - connections only allowed
15.04 | Testing & commissioning of H&C water installations incl. chlorination & certificate | item | 1 |  |  | Chlorination to BS EN 806 / L8 with lab sample
16.03 | Hot & cold water installation - accessible WC | item | 1 |  |  | Incl. TMV3, isolation, insulation
16.04 | Hot & cold water installation - WC (rear stair) | item | 1 |  |  | Incl. TMV3, isolation, insulation
16.05 | Hot & cold water installation - WC (adj. kitchen) | item | 1 |  |  | Incl. TMV3, isolation, insulation
16.06 | Hot & cold water installation - kitchen facility (sink, WHB, dishwasher points) | item | 1 |  |  | WH04 excluded per BOQ
16.14 | Water heater WH01 - HYCO IN30T 3kW, supply & install incl. expansion controls per detail | item | 1 |  |  | Electrical supply/isolator by electrician (BOQ 17.04)
18.42 | Water heater WH02 - HYCO IN30T 3kW (BOQ numbering error - should read 16.15) | item | 1
16.15 | Water heater WH03 - HYCO IN30T 3kW, supply & install incl. expansion controls per detail | item | 1
16.17 | Testing & commissioning of mechanical (plumbing) services | item | 1 |  |  | Pressure test & commissioning heaters/TMVs
TENDER TOTAL
Total labour hours

## Build-up
Price build-up per BOQ item
BOQ Ref | Description | Labour hours | Labour (£) | Materials net (£) | Materials inc. mark-up (£) | Labour inc. O&P (£) | Item price (£)
P1 | Plumbing preliminaries - RAMS, site set-up, travel/parking (Paisley town centre), consumables | 4
2.12 | Disconnect, remove & dispose of existing toilet, sink and plumbing pipework/fittings in WC's | 8
2.13 | Terminate and cap building services as required (plumbing services only) | 4
14.01 | WC adjacent to kitchen - supply & install sanitaryware (soft-close WC, standalone basin) | 6
14.03 | Soap dispenser attached to wall | 0.8
14.05 | WC adjacent to rear staircase - supply & install sanitaryware (soft-close WC, standalone basin) | 6
14.07 | Soap dispenser attached to wall | 0.8
14.10 | Accessible WC (cafe) - Doc M service pack, supply & install | 10
14.11 | Accessible WC - wall-hung pan: concealed frame & cistern (extra over Doc M pack) | 4
14.14 | Soap dispenser attached to wall | 0.8
15.01 | Drainage above ground - accessible WC (WC & basin) incl. NEW 110mm SVP, AAV & access | 16
15.02 | Drainage above ground - WC facilities (WC & basin) into existing SVP | 8
15.03 | Drainage above ground - kitchen (sink, WHB, dishwasher) into existing SVP | 8
15.04 | Testing & commissioning of H&C water installations incl. chlorination & certificate | 4
16.03 | Hot & cold water installation - accessible WC | 8
16.04 | Hot & cold water installation - WC (rear stair) | 6
16.05 | Hot & cold water installation - WC (adj. kitchen) | 6
16.06 | Hot & cold water installation - kitchen facility (sink, WHB, dishwasher points) | 8
16.14 | Water heater WH01 - HYCO IN30T 3kW, supply & install incl. expansion controls per detail | 4
18.42 | Water heater WH02 - HYCO IN30T 3kW (BOQ numbering error - should read 16.15) | 4
16.15 | Water heater WH03 - HYCO IN30T 3kW, supply & install incl. expansion controls per detail | 4
16.17 | Testing & commissioning of mechanical (plumbing) services | 4
TOTALS

## Materials
Materials take-off (from drawings E23025 (52) 001 BW3 & (53) 001 BW2) - rates are ESTIMATED trade prices, check with merchant
BOQ Ref | Section | Item | Qty | Unit | Rate (£) | Total (£)
P1 | Hot & cold water | Consumables - solder, flux, PTFE, solvent cement, fixings | 1 | lot | 150
P1 | General | Parking / travel allowance | 1 | item | 100
2.12 | Drainage | 110mm soil blanking caps | 2 | no | 6
2.12 | Drainage | Waste disposal / skip share - old sanitaryware | 1 | item | 150
2.13 | Hot & cold water | Stop ends 15/22mm | 8 | no | 3
14.01 | Drainage | 32mm bottle trap | 1 | no | 8
14.01 | Sanitaryware | Close-coupled WC pan, cistern & soft-close seat (commercial) | 1 | no | 180
14.01 | Sanitaryware | Silicone, pan & basin fixings | 1 | lot | 15
14.01 | Drainage | WC pan connector 110mm | 1 | no | 10
14.01 | Sanitaryware | Wash hand basin, tap & fixings | 1 | no | 150
14.03 | Sanitaryware | Wall-mounted soap dispenser | 1 | no | 25
14.05 | Drainage | 32mm bottle trap | 1 | no | 8
14.05 | Sanitaryware | Close-coupled WC pan, cistern & soft-close seat (commercial) | 1 | no | 180
14.05 | Sanitaryware | Silicone, pan & basin fixings | 1 | lot | 15
14.05 | Drainage | WC pan connector 110mm | 1 | no | 10
14.05 | Sanitaryware | Wash hand basin, tap & fixings | 1 | no | 150
14.07 | Sanitaryware | Wall-mounted soap dispenser | 1 | no | 25
14.10 | Drainage | 32mm bottle trap | 1 | no | 8
14.10 | Sanitaryware | Doc M pack (pan, basin, rails, lever tap) | 1 | no | 650
14.10 | Sanitaryware | Silicone, pan & basin fixings | 1 | lot | 15
14.10 | Drainage | WC pan connector 110mm | 1 | no | 10
14.11 | Sanitaryware | Concealed WC frame & cistern (wall-hung) | 1 | no | 250
14.14 | Sanitaryware | Wall-mounted soap dispenser | 1 | no | 25
15.01 | Drainage | 110mm 135 deg bend | 3 | no | 9
15.01 | Drainage | 110mm 92.5 deg bend | 3 | no | 9
15.01 | Drainage | 110mm Air Admittance Valve (Durgo) | 1 | no | 35
15.01 | Drainage | 110mm PVC-u soil pipe 3m | 4 | len | 28
15.01 | Drainage | 110mm access pipe | 1 | no | 20
15.01 | Drainage | 110mm fire collar 60 min | 1 | no | 25
15.01 | Drainage | 110mm floor pop-up connection | 1 | no | 15
15.01 | Drainage | 110mm pipe clips | 8 | no | 3
15.01 | Drainage | 110mm single branch | 1 | no | 18
15.01 | Drainage | 32mm bends (mixed) | 4 | no | 2.2
15.01 | Drainage | 32mm solvent waste pipe 3m | 1 | len | 8
15.01 | Drainage | 40mm bends (mixed) | 4 | no | 2.5
15.01 | Drainage | 40mm floor pop-up connection | 1 | no | 8
15.01 | Drainage | 40mm rodding eye / access plug | 2 | no | 5
15.01 | Drainage | 40mm solvent waste pipe 3m | 1 | len | 9
15.01 | Drainage | Boss adaptor 32/40mm | 1 | no | 5
15.01 | Drainage | Waste pipe clips 32/40mm | 10 | no | 0.6
15.02 | Drainage | 110mm 135 deg bend | 2 | no | 9
15.02 | Drainage | 110mm 92.5 deg bend | 2 | no | 9
15.02 | Drainage | 110mm PVC-u soil pipe 3m | 1 | len | 28
15.02 | Drainage | 110mm access pipe | 1 | no | 20
15.02 | Drainage | 110mm pipe clips | 5 | no | 3
15.02 | Drainage | 110mm single branch | 1 | no | 18
15.02 | Drainage | 110mm strap-on boss / stack connection | 1 | no | 12
15.02 | Drainage | 32mm bends (mixed) | 4 | no | 2.2
15.02 | Drainage | 32mm solvent waste pipe 3m | 1 | len | 8
15.02 | Drainage | 40mm rodding eye / access plug | 1 | no | 5
15.02 | Drainage | Boss adaptor 32/40mm | 1 | no | 5
15.02 | Drainage | Transition coupling to cast iron 110mm (Fernco) | 1 | no | 25
15.02 | Drainage | Waste pipe clips 32/40mm | 8 | no | 0.6
15.03 | Drainage | 110mm 135 deg bend | 1 | no | 9
15.03 | Drainage | 110mm 92.5 deg bend | 1 | no | 9
15.03 | Drainage | 110mm PVC-u soil pipe 3m | 2 | len | 28
15.03 | Drainage | 110mm fire collar 60 min | 1 | no | 25
15.03 | Drainage | 110mm floor pop-up connection | 1 | no | 15
15.03 | Drainage | 110mm pipe clips | 3 | no | 3
15.03 | Drainage | 110mm single branch | 1 | no | 18
15.03 | Drainage | 110mm strap-on boss / stack connection | 1 | no | 12
15.03 | Drainage | 32mm bottle trap | 1 | no | 8
15.03 | Drainage | 40mm bends (mixed) | 8 | no | 2.5
15.03 | Drainage | 40mm fire collar 60 min | 2 | no | 15
15.03 | Drainage | 40mm rodding eye / access plug | 1 | no | 5
15.03 | Drainage | 40mm sink trap c/w dishwasher spigot | 1 | no | 15
15.03 | Drainage | 40mm solvent waste pipe 3m | 3 | len | 9
15.03 | Drainage | 40mm tees | 3 | no | 3
15.03 | Drainage | 50 x 40mm reducer / connector | 2 | no | 4
15.03 | Drainage | 50mm solvent waste pipe 3m | 1 | len | 14
15.03 | Drainage | Transition coupling to cast iron 110mm (Fernco) | 1 | no | 25
15.03 | Drainage | Waste pipe clips 32/40mm | 12 | no | 0.6
15.04 | General | Chlorination & lab sample certificate (subcontract) | 1 | item | 350
16.03 | Hot & cold water | 15mm 1/4-turn isolating valve | 3 | no | 5
16.03 | Hot & cold water | 15mm copper tube 3m | 3 | len | 22
16.03 | Hot & cold water | 15mm elbows | 12 | no | 1.5
16.03 | Hot & cold water | 15mm equal tees | 3 | no | 2
16.03 | Hot & cold water | 15mm pipe clips | 18 | no | 0.4
16.03 | Hot & cold water | 22mm copper tube 3m | 1 | len | 38
16.03 | Hot & cold water | 22mm elbows | 3 | no | 3
16.03 | Hot & cold water | 22mm equal tees | 1 | no | 5
16.03 | Hot & cold water | 22mm pipe clips | 4 | no | 0.5
16.03 | Hot & cold water | 22mm reducing tees | 2 | no | 5
16.03 | Hot & cold water | Flexible tap / cistern connectors | 3 | no | 5
16.03 | Hot & cold water | Foil tape & BS1710 ID banding | 1 | lot | 10
16.03 | Hot & cold water | Foil-faced Class O insulation 15mm (per m) | 9 | m | 6
16.03 | Hot & cold water | Foil-faced Class O insulation 22mm (per m) | 3 | m | 7
16.03 | Hot & cold water | Straight couplers 15/22mm | 4 | no | 1.5
16.03 | Hot & cold water | TMV3 thermostatic mixing valve 15mm | 1 | no | 65
16.04 | Hot & cold water | 15mm 1/4-turn isolating valve | 3 | no | 5
16.04 | Hot & cold water | 15mm copper tube 3m | 3 | len | 22
16.04 | Hot & cold water | 15mm elbows | 10 | no | 1.5
16.04 | Hot & cold water | 15mm equal tees | 3 | no | 2
16.04 | Hot & cold water | 15mm pipe clips | 16 | no | 0.4
16.04 | Hot & cold water | 22mm copper tube 3m | 2 | len | 38
16.04 | Hot & cold water | 22mm elbows | 4 | no | 3
16.04 | Hot & cold water | 22mm equal tees | 1 | no | 5
16.04 | Hot & cold water | 22mm full-bore isolating valve (incoming main) | 1 | no | 12
16.04 | Hot & cold water | 22mm pipe clips | 7 | no | 0.5
16.04 | Hot & cold water | 22mm reducing tees | 2 | no | 5
16.04 | Hot & cold water | Automatic air vent | 1 | no | 12
16.04 | Hot & cold water | Drain-off cock 15mm | 1 | no | 5
16.04 | Hot & cold water | Flexible tap / cistern connectors | 3 | no | 5
16.04 | Hot & cold water | Foil tape & BS1710 ID banding | 1 | lot | 10
16.04 | Hot & cold water | Foil-faced Class O insulation 15mm (per m) | 9 | m | 6
16.04 | Hot & cold water | Foil-faced Class O insulation 22mm (per m) | 5 | m | 7
16.04 | Hot & cold water | Straight couplers 15/22mm | 4 | no | 1.5
16.04 | Hot & cold water | TMV3 thermostatic mixing valve 15mm | 1 | no | 65
16.05 | Hot & cold water | 15mm 1/4-turn isolating valve | 3 | no | 5
16.05 | Hot & cold water | 15mm copper tube 3m | 3 | len | 22
16.05 | Hot & cold water | 15mm elbows | 10 | no | 1.5
16.05 | Hot & cold water | 15mm equal tees | 3 | no | 2
16.05 | Hot & cold water | 15mm pipe clips | 16 | no | 0.4
16.05 | Hot & cold water | 22mm reducing tees | 3 | no | 5
16.05 | Hot & cold water | Flexible tap / cistern connectors | 3 | no | 5
16.05 | Hot & cold water | Foil tape & BS1710 ID banding | 1 | lot | 10
16.05 | Hot & cold water | Foil-faced Class O insulation 15mm (per m) | 9 | m | 6
16.05 | Hot & cold water | Straight couplers 15/22mm | 3 | no | 1.5
16.05 | Hot & cold water | TMV3 thermostatic mixing valve 15mm | 1 | no | 65
16.06 | Hot & cold water | 15mm 1/4-turn isolating valve | 5 | no | 5
16.06 | Hot & cold water | 15mm copper tube 3m | 3 | len | 22
16.06 | Hot & cold water | 15mm elbows | 13 | no | 1.5
16.06 | Hot & cold water | 15mm equal tees | 3 | no | 2
16.06 | Hot & cold water | 15mm pipe clips | 20 | no | 0.4
16.06 | Hot & cold water | 22mm copper tube 3m | 2 | len | 38
16.06 | Hot & cold water | 22mm elbows | 5 | no | 3
16.06 | Hot & cold water | 22mm equal tees | 2 | no | 5
16.06 | Hot & cold water | 22mm full-bore isolating valve (incoming main) | 1 | no | 12
16.06 | Hot & cold water | 22mm pipe clips | 9 | no | 0.5
16.06 | Hot & cold water | 22mm reducing tees | 3 | no | 5
16.06 | Hot & cold water | Automatic air vent | 1 | no | 12
16.06 | Hot & cold water | Dishwasher valve 15mm | 1 | no | 6
16.06 | Water heaters | Double check valve 15mm | 1 | no | 12
16.06 | Hot & cold water | Drain-off cock 15mm | 2 | no | 5
16.06 | Hot & cold water | Flexible tap / cistern connectors | 5 | no | 5
16.06 | Hot & cold water | Foil tape & BS1710 ID banding | 1 | lot | 10
16.06 | Hot & cold water | Foil-faced Class O insulation 15mm (per m) | 9 | m | 6
16.06 | Hot & cold water | Foil-faced Class O insulation 22mm (per m) | 6 | m | 7
16.06 | Hot & cold water | Straight couplers 15/22mm | 4 | no | 1.5
16.06 | Hot & cold water | TMV3 thermostatic mixing valve 15mm | 1 | no | 65
16.14 | Hot & cold water | 15mm 1/4-turn isolating valve | 3 | no | 5
16.14 | Water heaters | Check valve 15mm | 1 | no | 8
16.14 | Water heaters | Dielectric union 15mm | 2 | no | 8
16.14 | Water heaters | HYCO IN30T 3kW instantaneous water heater | 1 | no | 230
16.14 | Water heaters | Potable expansion vessel 3.5 bar | 1 | no | 35
16.14 | Water heaters | Pressure reducing valve 3.5 bar 15mm | 1 | no | 35
16.14 | Water heaters | Pressure relief valve 6 bar + tundish | 1 | no | 30
18.42 | Hot & cold water | 15mm 1/4-turn isolating valve | 3 | no | 5
18.42 | Water heaters | Check valve 15mm | 1 | no | 8
18.42 | Water heaters | Dielectric union 15mm | 2 | no | 8
18.42 | Water heaters | HYCO IN30T 3kW instantaneous water heater | 1 | no | 230
18.42 | Water heaters | Potable expansion vessel 3.5 bar | 1 | no | 35
18.42 | Water heaters | Pressure reducing valve 3.5 bar 15mm | 1 | no | 35
18.42 | Water heaters | Pressure relief valve 6 bar + tundish | 1 | no | 30
16.15 | Hot & cold water | 15mm 1/4-turn isolating valve | 3 | no | 5
16.15 | Water heaters | Check valve 15mm | 1 | no | 8
16.15 | Water heaters | Dielectric union 15mm | 2 | no | 8
16.15 | Water heaters | HYCO IN30T 3kW instantaneous water heater | 1 | no | 230
16.15 | Water heaters | Potable expansion vessel 3.5 bar | 1 | no | 35
16.15 | Water heaters | Pressure reducing valve 3.5 bar 15mm | 1 | no | 35
16.15 | Water heaters | Pressure relief valve 6 bar + tundish | 1 | no | 30
16.17 | General | Test gauge / commissioning consumables | 1 | lot | 20
TOTAL

## Qualifications
Tender qualifications, exclusions & programme
Tender basis
BOQ - Ground Floor Fit Out - Light House rev3; Tender Clarifications No.1 & No.2.
Drawings: Kilbryde E23025 (52) 001 BW3 (above ground drainage), E23025 (53) 001 BW2 (hot & cold water); Framed Estates 697 AB 111C (GF plan), 697 AB 400A (accessible WC).
Prices exclude VAT - domestic reverse charge applies. Subject to CIS. Tender valid for 30 days.
Contract: Minor Works Building Contract for use in Scotland. Payment by monthly valuation.
Items excluded / by others
BOQ ref | Item | Comment
14.02 / 14.06 / 14.13 | Hand dryers | Supply by PC sum; install & wiring by electrician
14.04 / 14.08 / 14.12 | Mirrors & colostomy shelves | By joiner - can supply & fix on request
16.01 | Door transfer grilles | By joiner / ventilation - can price on request
16.08 - 16.11 | Extract fans DEF01/DEF02 & ductwork | By ventilation / electrician - can price on request
16.12 / 16.16 | Kitchen extract KEP01 & water heater WH04 | Excluded in BOQ
17.x | All electrical works incl. isolators & spurs to water heaters | By electrician
18.1 | Builders work in connection (holes, boxing-in, access panels, lifting/relaying floors, making good) | By main contractor
GT01 | Grease trap supply (Big Dipper W-250-ISE) - shown on drawing, not in BOQ | Connections allowed in 15.03; supply can be priced on request
Assumptions & clarifications
1. Existing SVP is sound and suitable for new connections; transition couplings allowed for connection to cast iron. Replacement of existing stack excluded.
2. Two incoming 22mm mains are marked 'TBC' on drawing (53) 001 - allowed for connection within 3m of fitting positions. Alterations to incoming supply/meter excluded.
3. Below-floor drainage assumes access via the suspended timber floor; lifting and relaying of flooring by main contractor/joiner.
4. Sanitaryware priced as standard commercial range (Twyford / Armitage Shanks or equal). Client-selected ranges to be adjusted.
5. Item 14.11: BOQ calls for a wall-hung pan in the accessible WC. A concealed frame is priced separately so it can be omitted if a close-coupled Doc M pan is accepted.
6. Water heaters: expansion controls (PRV, check valve, expansion vessel, relief valve) priced per the typical detail on drawing (53) 001. These are not normally required on instantaneous IN30T heaters - saving available if omitted.
7. Fire collars allowed where drainage passes through fire-rated construction (drawing note 8). General fire stopping by others (BOQ 13.06).
8. Items 15.04 and 16.17 (testing & commissioning) appear twice in the BOQ - priced once each without duplication: 15.04 = chlorination & certificate, 16.17 = pressure testing & commissioning.
9. Kitchen scope is TBC in the BOQ - 15.03 and 16.06 allow first fix & connections to sink, WHB and dishwasher positions shown on the drawings. Kitchen equipment, grease trap supply and WH04 excluded.
10. Works carried out during normal working hours (Mon-Fri, 8am-5pm) with clear access.
Programme
Lead-in: 2 weeks from receipt of order.
Plumbing on site: approx. 5 days 1st fix (strip-out, drainage, pipework) and 3 days 2nd fix (sanitaryware, heaters, testing, commissioning) - 2 operatives.
Suggested overall contract duration for the fit-out: 8-10 weeks.