## Material List
Life Church – Ground Floor Fit Out, 6-8 High Street, Paisley
Plumbing material take-off from Kilbryde E23025 (52) 001 BW3, (53) 001 BW2 & Framed Estates 697 AB 111C / 400A. Drawings are 1:50 schematic – quantities include c.15% waste; check on site.
Section | Item / Description | Qty | Unit | Basis | Notes / Queries | Rate (£) | Total (£)
DRAINAGE ABOVE GROUND (Dwg E23025 (52) 001 BW3)
Soil pipe | 110mm PVC-u solvent weld soil pipe, 3m lengths | 7 | no | Measured c.18m (6.3m low level, 7.7m below floor, c.4.5m new stack) + 15% | New 110 SVP at rear WC; below-floor runs from pop-ups back to existing SVP
Soil fittings | 110mm 92.5° bends | 6 | no | Allowance
Soil fittings | 110mm 135° (45°) bends | 6 | no | Allowance | Below-floor diagonal runs
Soil fittings | 110mm single branch (88° / swept) | 3 | no | WC connections
Soil fittings | 110mm access pipe / inspection port | 2 | no | Dwg note 5 – access to all stacks | Access panels by builder at 1200 AFFL
Soil fittings | 110mm strap-on boss / connection to existing SVP | 2 | no | Drawing | Check existing SVP material on site (cast iron?)
Soil fittings | Cast-iron to PVC transition coupling (e.g. Fernco) 110mm | 2 | no | Provisional | Only if existing stack is cast iron
Soil fittings | 110mm Air Admittance Valve (internal, e.g. Durgo) | 1 | no | Drawing – 'New 110mm AAV' | Boxed in with access panel (dwg note 4)
Soil fittings | 110mm floor pop-up / rise-from-below connection | 2 | no | Drawing – 2 no. 'New 110mm pop-up'
Soil fittings | WC pan connector 110mm (straight/offset) | 3 | no | 3 no. WCs
Soil fittings | 110mm pipe clips / brackets | 16 | no | Allowance
Soil fittings | 110mm fire collar (60 min) | 2 | no | Provisional – dwg note 8 | Where pipe passes fire-rated wall
Waste pipe | 40mm solvent weld waste pipe, 3m lengths | 4 | no | Measured c.8m (3.5m below floor, c.4.5m low level) + 15%
Waste pipe | 32mm solvent weld waste pipe, 3m lengths | 2 | no | WHB branches
Waste pipe | 50mm solvent weld waste pipe, 3m length | 1 | no | Grease trap 50mm in/out
Waste fittings | 40mm bends 90°/135° (mixed) | 12 | no | Allowance
Waste fittings | 32mm bends 90°/135° (mixed) | 8 | no | Allowance
Waste fittings | 40mm tees / swept tees | 3 | no | Allowance
Waste fittings | 40mm rodding eye / access plug | 4 | no | Drawing – 4 no. '40Ø RE'
Waste fittings | 40mm floor pop-up connection | 1 | no | Drawing – 'New 40mm pop-up'
Waste fittings | Boss adaptors 32/40mm to 110 stack | 2 | no | Allowance
Waste fittings | 50mm to 40mm reducers / connectors | 2 | no | Grease trap connections
Waste fittings | 32mm bottle trap (75mm seal) | 4 | no | 4 no. WHBs (3 WCs + kitchen)
Waste fittings | 40mm sink trap with dishwasher spigot | 1 | no | Kitchen sink + DW
Waste fittings | Waste pipe clips 32/40mm | 30 | no | Allowance
Waste fittings | 40mm fire collar (60 min) | 2 | no | Provisional – dwg note 8
HOT & COLD WATER (Dwg E23025 (53) 001 BW2)
Copper pipe | 22mm copper tube (Table X), 3m lengths | 5 | no | Measured c.9.6m of 22mm MWS + incomers (TBC) + 15% | 2 no. incoming 22mm MWS 'TBC' – length unknown
Copper pipe | 15mm copper tube (Table X), 3m lengths | 12 | no | c.7m horizontal branches + c.25m drops to 14 outlets + 15% | Drops from high level not shown on plan – allowance
Copper fittings | 22mm elbows | 12 | no | Allowance | Endfeed or press-fit – your choice
Copper fittings | 22mm equal tees | 4 | no | Allowance
Copper fittings | 22 x 15 x 15 / 22 x 22 x 15 reducing tees | 10 | no | Allowance
Copper fittings | 15mm elbows | 45 | no | Allowance
Copper fittings | 15mm equal tees | 12 | no | Allowance
Copper fittings | Straight couplers 15/22mm | 15 | no | Allowance
Valves | 22mm full-bore isolating valve (incoming mains) | 2 | no | 2 no. incoming MWS
Valves | 15mm ¼-turn isolating valve (Ball-o-fix type) | 23 | no | Dwg note 5 – every outlet (14) + 3 per heater (9)
Valves | Drain-off cock 15mm | 3 | no | Dwg note 6 – low points
Valves | Automatic air vent | 2 | no | Dwg note 6 – high points
Valves | TMV3 thermostatic mixing valve 15mm | 4 | no | Drawing – 4 no. TMV (WHBs) | TMV3 cert needed for accessible WC
Valves | Double check valve 15mm | 1 | no | Kitchen / dishwasher feed
Water heaters | HYCO IN30T 3kW instantaneous water heater | 3 | no | WH01, WH02, WH03 | WH04 (SF10K kitchen) EXCLUDED in BOQ
Water heaters | Pressure reducing valve set 3.5 bar, 15mm | 3 | no | Heater detail – 1 per heater | Query: expansion kit usually not needed on instantaneous heater
Water heaters | Check valve 15mm | 3 | no | Heater detail
Water heaters | Potable expansion vessel (3.5 bar precharge), small | 3 | no | Heater detail | Query as above
Water heaters | Pressure relief valve 6 bar + tundish / discharge to drain | 3 | no | Heater detail
Water heaters | Dielectric unions 15mm | 6 | no | Heater detail – 2 per heater
Connections | Flexible tap connectors 15mm x ½" / cistern connectors | 14 | no | WHBs, sink, WCs
Connections | Dishwasher valve / washing-machine type valve 15mm | 1 | no | Kitchen DW
Clips & sundries | 15mm pipe clips | 70 | no | Allowance
Clips & sundries | 22mm pipe clips | 20 | no | Allowance
Insulation | Foil-faced Class 'O' pipe insulation, 15mm (BS5422) | 36 | m | Dwg note 9 – all H&C pipework
Insulation | Foil-faced Class 'O' pipe insulation, 22mm (BS5422) | 14 | m | Dwg note 9
Insulation | Foil tape + BS1710 pipe ID banding / labels | 1 | lot | Dwg note 9
Test & commission | Chlorination / disinfection (BS6700 / L8) + water sample cert | 1 | item | Dwg note 8 & 10 | Kit or subcontract
SANITARYWARE & FIT-OFF (BOQ 14 / Dwg 697 AB 111C & 400A)
Sanitaryware | Close-coupled WC pan, cistern & soft-close seat | 2 | no | BOQ 14.01 & 14.05
Sanitaryware | Wash hand basin (standalone) + tap | 2 | no | BOQ 14.01 & 14.05
Sanitaryware | Doc M pack – accessible WC (pan, basin, rails, lever tap) | 1 | no | BOQ 14.10 | BOQ 14.11 says WALL-HUNG pan – check if frame needed
Sanitaryware | Concealed WC frame / cistern (if wall-hung) | 1 | no | Provisional – BOQ 14.11
Sanitaryware | Wall-mounted soap dispensers | 3 | no | BOQ 14.03 / 14.07 / 14.14 | Confirm your package
Sanitaryware | Mirror + 250x150 colostomy shelf | 3 | no | BOQ 14.04 / 14.08 / 14.12 | Confirm your package – joiner?
Sanitaryware | Silicone, pan fixings, basin fixings | 1 | lot | Allowance
KITCHEN (shown on drawings – scope TBC in BOQ)
Kitchen | Kitchen wash hand basin | 1 | no | Shown on (52) & (53) | Not in BOQ – query
Kitchen | Stainless steel kitchen sink | 1 | no | Shown on drawings | Probably in £12,500 kitchen P.Sum – query
Kitchen | Grease trap GT01 – Big Dipper W-250-ISE (648x615x477, 230V) | 1 | no | Dwg (52) schedule | Not in BOQ – query who supplies
Kitchen | HYCO SF10K 10L water heater (WH04) | 0 | no | Dwg (53) | EXCLUDED in BOQ – qty 0
STRIP-OUT & GENERAL
Strip-out | Push-fit / solder stop-ends 15/22mm | 8 | no | BOQ 2.12 / 2.13
Strip-out | 110mm soil blanking caps | 2 | no | BOQ 2.12
Strip-out | Skip / waste disposal – old sanitaryware | 1 | item | BOQ 2.12
Consumables | Solder, flux, PTFE, jointing compound, solvent cement, cleaner, fixings | 1 | lot | Allowance
TOTAL